## Sheet1
Calculation of Excess PV Power from Solar Array
(((($B$4-$B$9)*($B$10/100)+1)*$B$11)*($B$5/$B$12))-$B$6
f_tempinput - Panel Temperature of Array from Sensor | 27 | C
f_irrinput - Measured Solar Irradiance from Sensor | 500 | WM2
f_Pvcurrentoutput - Measured Current PV output from MODBUS connection to Solar System Control Computer(CCGX) | 200 | Watts
Constants
c_stctemp - STC Test Temperature for Panel | 25 | C
c_tempcoff - Temperature Cofficient for Panel as Percent per Degree C | -0.3 | %
c_pvwatts - Power of entire array at STC | 1400 | Watts
c_stc_irr - STC Test Irradiance | 1000 | WM2
TOTAL EXCESS POWER | 495.8 | Watts
Calculation Breakdown
f_tempinput - c_stctemp Temperature Differential | 2 | Deg C
(B17*c_tempcoff/100)+1 Percentage Differential of Pmax Based on Temperature | 0.994 | %
B18*c_pvwatts Solar Array Potential Power based on Temperature | 1391.6 | Watts
B19*(f_irrinput/c_stc_irr) Solar Array Potential Adjusted for Current Solar Irradiance | 695.8 | Watts
B20-f_Pvcurrentoutput Available Solar Power based on Current PV Load | 495.8 | Watts
You can only change the values in Green - The rest of the sheet is locked